DEENDAYAL PORT AUTHORITY

(Formerly known as Kandla Port Trust)

Office of the Electrical Engineer,

Port & Customs Building, 						Tel: (02836)270209 / 270342

New Kandla (Kutch), Gujarat-370210.				FAX: (02836) 270184 /270475

No.EL/AC/2060     				 			                      Date:  26/11/2022

To

M/s. ______________________.,

___________________________,

___________________________,

___________________________.

“EXPRESSION OF INTEREST (EOI)”

Subject – “Procurement of 4 Nos. 3 KVA UPS system along with Voltage stabilizer for Railway weighbridges CCTV at inside cargo jetty area”

Sir,

Expression of interest (EOI) are invited to carry out the work “Procurement of 4 Nos. 3 KVA UPS system along with Voltage stabilizer for Railway weighbridges CCTV at inside Cargo Jetty Area” as per the Scope of work, Technical specification, Terms &, Conditions stipulated below.

The Expression of Interest (EOI) along with Schedule-B should reach this office of undersigned on or before 10/12/2022 at 17.00hrs or scanned copy of scanned offer also accepted on e-mail xenedpt@gmail.com which shall be opened on the same day.

Yours faithfully,

S/d-

Executive Engineer (E)

Deendayal Port Authority.

## “Schedule B”

| Sr. No. | Description | Qty. | Unit | Rate per Year per Crane |  | Total Amount |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | In figure | In words |  |
| 1 | Supply of Electronic Servo Controlled Voltage Stabilizer as per Technical Specification No.1 | 4 | Nos. |  |  |  |
| 2 | Supply of 3 KVA UPS system including batteries as per technical specification No.2 | 4 | Nos. |  |  |  |
| Total Amount: Rs.: |  |  |  |  |  |  |

Note (Only Rs. ___________________________________________________)

Inclusive of all taxes, transportation & incidental charges etc. but excluding of GST.

S/d-

Signature & Seal 					                         Executive  Engineer (E)

of Contractor                                                                     Deendayal Port Authority

SCOPE OF WORK

### General:

4 Nos. of Railway weighbridges are installed in cargo jetty area at Deendayal Port Authority. The weighbridges are consisting of networking Rack, CCTV cameras etc. which required regulated uninterrupted power supply.

Deendayal Port Authority (DPA) intends to install Voltage stabilizer & UPS system for uninterrupted power supply to all Railway weighbridges inside cargo jetty area.

### Technical Specification No.1:

The specification of Electronic Servo Controlled Voltage Stabilizer as following:

| Sr. No. | Description | Offer value |
| --- | --- | --- |
| 1 | Capacity | 5 KVA/single Phase. |
| 2 | Regulator engine | High frequency 20Khz IGBT driven voltage regulation convertor |
| 3 | Input Normal Voltage | 230 Voltage AC Single phase |
| 4 | Input Normal operating voltage range (typical output regulation within +/- 15 of nominal) | 140 – 300 voltage AC |
| 5 | Input Nominal frequency | 47- 63 Hz |
| 6 | Output Power efficiency (with 20-100% load condition & worst incoming voltage) | Over 95% |
| 7 | Output Nominal Voltage | 230 Voltage Ac Single phase |
| 8 | Output Voltage regulation (typical, excluding meter error) | +/-1% |
| 9 | Annunciation | LED display for regulation mode, Bypass mode & fault Condition. |
| 10 | Ambient temperature | 00 to 500 centigrade (320 to 1130 farhenite). 10 to 90% RH non-condensing |
| 11 | Cooling Method | Natural Cooled |
| 12 | Standers & Safety | Designed to meet URL 60950-l standards. Protection class lP 20 |
| 13 | Overload & Short circuit Protection | Through suitably rated input circuit breaker. |
| 14 | Soft Switch-On | This feature ensure that the output voltage is will not be higher than the input voltage upon switch-on Till commencement full stabilization |
| 15 | Automatic bypass | Regulator engine will be automatically bypass when there is a fault condition. |
| 16 | Surge test conditions | Per class 2 Surge ( combination wave) |
| 17 | Surge let – through voltage | 1.2 x 50µs, 6 kv, 8 x 20µs, 3 kA wavefrom, L-N < 300V |
| 18 | Wavefrom (Batt. Mode) | Pure Sinewave |

OPTIONAL FEATURE:

Digital Voltmeter

Digital line frequency Meter / Trip Unit

Ammeter

RF Supressor

Manual Start facility

Audio Alarm

Input MCCB

Standards & Sefety

Overload & Short circuit Protection

Soft Switch ON

PRINCIPAL OF OPERATION:

Electronic Servo Controlled Voltage Stabilizer delivers continuous output within ± 1% of the set value over the specified input range. It has high efficiency and does not introduce any waveform distortion. The over-voltage /under-voltage protection circuit shuts off the output when it exceeds the set limit. Electronic overload protection circuit protects the stabilizer from over loading and avoids damage. Basically, it contains a continuously variable Auto Transformer (Auto stat), Buck-boost transformer, A.C. Synchronous motor and IC version sensing/control circuit. The input voltage is applied across the winding of the Auto stat. the primary winding of the Buck-boost transformer is connected between the fixed tap and variable tap of the Autostat. Depending on the polarity with respect to the input voltage the induced secondary voltage of the Buck-Boost transformer adds or subtracts to the input voltage and gives the stabilized output voltage within ± 1%. The position of the brush on the Autostat changes according to the changes in the input voltage and thus corrects the output for the entire input voltage range.

The brush carriage of the Autostat is coupled to the synchronous Motor through a reduction gear. The motor and control circuit forms the closed loop control system. The control circuit senses the output voltage and compares with the reference signal continuously. In case of deviation in the output, it generates an error signal that triggers the triacs (static switches) which in turn energizes the motor to rotate the arm of the Autostat in the desired direction to bring the output voltage to the set point.

The supply at site with installation & commissioning which also includes with transportation at Kandla and inclusive of all taxes except GST.

### Technical Specification No.2:

supply at site of 3 KVA UPS system as following specification:

| Sr. No. | Description | offer value |
| --- | --- | --- |
| 1 | Configuration | Single Phase with Ground |
| 2 | Capacity | 3 KVA Online UPS |
| 3 | Capacity | 2.4 KW |
| 4 | Input |  |
|  | Nominal Voltage | 200/208/220/230/240 V AC |
|  | Input Voltage Range | 110- 300 V AC (at 50% Load or 160-280 V AC (at 100% Load) |
|  | Frequency Range | 40Hz -70 Hz |
|  | Power factor | ≥ 0.99 @ Nominal Voltage (100% Load) |
| 5 | Output |  |
|  | Output Voltage | 200/208/220/230/240 V AC |
|  | Voltage Regulation | ± 1% |
|  | Frequency Range (synchronized Range) | 47 – 53 Hz |
|  | Frequency Range (Batt. Mode) | 50 Hz ±0.25 Hz |
|  | Current Crest Ratio | 3:1 |
|  | Harmonic Distortion | ≤ 3 % THD (Linear Load) ≤ 6 % THD (Non-Linear Load) |
|  | Waveform (Batt. Mode) | Pure Sinewave |
|  | Over Load | 105% - 110%: 10mins, 110%-130%-1min: >130%-3 sec |
| 6 | Efficiency |  |
|  | AC Mode | 90% |
| 7 | Battery (Long Run Model) |  |
|  | Battery Type | Dry type (maintenance free) 100 Ah |
|  | Backup | 5 to 7 Hours. |
|  | Charging Current (max.) | 1A/2A/4A/6A (Adjustable) |
|  | Additional Charger | 12 A |
| 8 | Indicator |  |
|  | LCD | Low level, Battery level, AC Mode, Battery Mode, Bypass Mode, and Fault indication |
| 10 | Enviroment |  |
|  | Humidity | 20-90% RH @ 0-40ºC (Non-condensing) |
|  | Noise Level | Less than 58dB @1 Meter |
| 11 | Magement |  |
|  | Smart RS-232/USB | Support Windows@2000/2003/XP/Vista/2008. Windows @ 7/8. Linux and MAC |
|  | Optional RS-485 | SNMP, Modbus (RS485) and Potential free Contact |

The UPS system along with Dry type Battery (maintenance free) including battery stands, battery link, connecting leads & wires, necessary nut & bolts shall be supplied by supplier and installation & commissioning which also includes with transportation at Kandla and inclusive of all taxes except GST shall be in the scope of supplier as per direction of Engineer In-charge.

Signature & Seal 					  		       Executive  Engineer (E)

of Contractor                                                                                                  Deendayal Port Authority

GENERAL TERMS AND CONDITION.

- The work shall be carried out inside Cargo Jetty Area. Necessary entry permit is to be arranged by Contractor

- The Contractor shall arrange all Tools and Tackles for execution of work.

- The contractor shall have the full knowledge of the site of the work and local conditions before commencing the work and no claim whatsoever will be entertained for any nature of work arising out of local conditions.

- Necessary Indian Dock Safety regulation for safety purpose shall be adhered by the contractor and he will be held responsible for any violation of the same and contractor has to supply all required PPE to his workman.

- The Contractor will ensure that his labour shall strictly adhere to all safety measures during the execution of work so as to avoid any accident.

- The Materials supplied should as per original as per IS.

- The work includes all material & labour as directed by Engineer-In-Charge.

- Force Majeure. this will be restricted to natural calamities and acts of God only.

14.Terms of Payment

All payment shall be made in Indian rupees unless specifically mentioned.

- 70% payment released after material received at site in good conditions.

- 30% payment will be released after completion of the work i.e. Installation & commissioning.

The payment will be made through RTGS.

- Income Tax shall be deducted at source from the payment of bill as applicable.

- Liquidated Damages:

Liquidated Damages shall be levied at the rate of 0.5% (per week) of contract value for delay of each week or part thereof subject to maximum of 10% of contract value in the event of failure to complete the work in the stipulated period of completion or such extension as may be granted.

- Guarantee:

The guarantee period shall be valid up to 18 (Eighteen) months with effect from the date of acceptance of the materials by DPA or 12 (twelve) months from the date of installation, whichever is earlier.

S/d-

Signature & Seal 					  		       Executive  Engineer (E)

of Contractor                                                                                                  Deendayal Port Authority

| Approved Make List for Electronic Items |  |  |
| --- | --- | --- |
| Sr. No. | Description | Recommended Makes |
| 1 | UPS of 3 KVA | Fuji Electric/Unitech/Luminous/Hitachi/Genus/Sukan/ Microtak |
| 2 | Voltage Stabilizer | Veeline/ Capri/Jindal Electric/ Microtek/Servomax |
| 3 | Battery of Dry Type | Exide/HBL/Luminous/Amaron/Microtax |

Seal & Sign                                                         Executive Engineer (E)

Contractor                                                       Deendayal Port Authority