DEENDAYAL PORT AUTHORITY

Office of the  Engineer,

Electrical Division,

Nirman Building Ground floor, 	                                       Tel: (02836)270209 270342

New Kandla (Kutch), Gujarat-70210.                                FAX: (02836) 270184 /270475

No. EL/WK/2876/EOI                                                                    Dated 14.11.2025

To,

M/s.

“EXPRESSION OF INTERSET (EOI)”

Sub. : “Annual rate Contract for Supply & laying of HT/LT underground cables, HT/LT cable fault finding at inside cargo jetty area.”

Sir,

(This EOI is issued to elicit Expression of Interest from the parties interested in the work and does not constitute any binding commitment from the Deendayal Port Authority to proceed with the work or invite any or all the parties in the subsequent bidding process. (The Open Tenders will be issued subsequently.)

Executive Engineer (Electrical), DPA invites Expression of Interest for the work of “Annual rate Contract for Supply & laying of HT/LT underground cables, HT/Lt cable fault finding at inside cargo jetty area” from the reputed firms from those who have executed similar work in Government / Public Sector and other leading private organizations. The Expression of Interest (EOI) documents containing details of Scope of Work and Technical Specifications are enclosed herewith.

The interested firms are requested to submit their Expression of Interest (EOI) for the said work in BOQ format as enclosed, along with credential for similar nature of work & firm GST No. The EOI shall be submitted to the office the undersigned on or before 01/12/2025. A soft copy of EOI is also acceptable through e- mail Id Deepak.hazra@deendayalport.gov.in & anil.rautiya@deendayalport.gov.in

Yours faithfully,

Sd/-

Executive Engineer (E)

Deendayal Port Authority

Scope of Work & Technical Specification

The scope of work envisages the following:

- All the complaints/faults shall be attended on 7 X 24 Hrs. basis on comprehensive manner to restore the power supply.

- If any of the materials, which are not in the scope of the contractor, then the contractor shall bring the materials after taking clearance from EIC and the payment for the materials will be reimbursed by DPA subject to submission original invoice from OEM/Authorized Dealer/Authorized Channel Partner. However, for purchasing the materials on urgency from OEM/Authorized Dealer/Authorized Channel Partner, the contractor shall take prior permission from EIC. The procurement of materials shall be OEM materials only.

- Cable shall be supplied, inspected, laid, tested and commissioned in accordance with specification, relevant Indian Standards specifications and cable manufacturer’s instructions. The cable shall be delivered at site in original drums with manufacturer’s name clearly written on the drums. The recommendations of the cable manufacturer with regard to jointing and sealing be strictly followed.

- Cable Handling and Laying

Ensure that both ends of cable are properly sealed to prevent ingress / absorption of moisture. Before removing of cable from the drum, mount the latter properly on jacks or cable wheels.

- The work shall be carried out keeping in mind the aesthetic requirement of individual site and matching of final work with the surrounding by proper finishing as necessary to maintain uniformity.

- During fault finding of LT/HT cable disconnection of end termination kit at respective substation will be in the scope of contractor with all required labor, tools & material.

- Contractor shall deposit / Hand over the old /unused cables from the existing route in sub division store. The tenderers shall quote the rate for cable laying which shall include the route marker (HT/LT laying), cable tagging, dressing, removing the old unused cable from the RCC trench, end termination, appropriate size of gland & ferrule work as per requirement etc.

- Contractor shall depute the Authorized Electrical Engineer with Supervisor Certificate, who will remain on the job continuously during execution of work. In absence of Authorized Person, the work will not be allowed to carry out further and no compensation will be entitled for non- working or idle men power. In the event of any accident or damage / theft, same shall be borne by the contractor. DPT will not entertain any claim in this regard.

- While crossing the rail / road, damaged caused to it should be set right by the contractor to the satisfaction of the Executive Engineer (Harbour), Deendayal Port Authority.

- Before laying the new cables at existing route through Road / rail/ jetty, contractor shall take written permission from Engineer In-Charge, in this regard contractor shall make earmarked drawing in two sets, which will clearly indicate the route cable will pass and take permission.

- Tools & tackles, Man power & Material, Vehicle etc. will be arranged by contractor to execute the work. No facility will be provided by DPA and will not entertain any claim against it. Moreover, the cable fault Detector to be kept at site 24x7 with pre-fault locator, route tracer, surge generator surge wave receiver & pin point fault locator complete set for fault finding of cable.

Technical Specification No.1

This includes supply of 3 Core Stranded Compacted Aluminium Conductor, Conductor Screen with Extruded Semi Conducting compound, XLPE insulated, Insulation Screening with extruded semi conducting compound in combination with copper tape, cores laid up, innersheath of PVC, Galvanised steel flat strip armoured & overall PVC sheathed cable conforming to IS 7098 (Part – II) with up to date Amendments of following size.

  - 3C X 150 Sq. mm (E) XLPE Insulated

  - 3C X 300 Sq. mm (E) XLPE Insulated

  - 3C X 400 sq. mm (E) XLPE Insulated

Technical Specification No. 2

Supply of XLPE Insulated, 4 Core 1.1 KV LT, cores laid up PVC Inner sheathed, armoured, with extruded PVC Aluminium conductor cable as per IS-7098(Part I) 1988 with up to date amendment as per following size.

- 4C X 16 Sq.mm XLPE Insulated.

- 4C X 25 Sq.mm XLPE Insulated.

- 4C X 35 Sq.mm XLPE Insulated.

- 4C X 50 Sq.mm XLPE Insulated

- 4C X 70 Sq.mm XLPE Insulated.

- 4C X 95 Sq.mm XLPE Insulated

- 4C X 150 Sq.mm XLPE Insulated

- 4C X 300 Sq.mm XLPE Insulated

Technical Specification No. 3

This includes laying of up to 3C x 70 to 185 Sq.mm HT armored aluminium Conductor XLPE Cable of 11KV Grade (excluding supply of cable) through.

  - Through RCC Trench

The cable shall be laid after opening of RCC trench by removing the RCC Covers either through manpower or earthmover & cable trench shall be cleaned properly including removal of garbage, stones, bricks & old unused cables etc from the trench line without damaging the other cables laying in the trench. After laying of the cable, cable trench shall be properly covered with removed RCC covers as per original. The contractor shall provide heat shrinkable straight through joint of relevant size of approved make if the laying of cable shall be more than standard drum length, the straight through joint shall not be considered in the quantity of Item no. 7 & 8 of Schedule - B. This includes all labour and material as directed by Engineer-in-Charge.

  - Through Hard & soft soil

This includes laying of cable up to 3 core 70 to 185 Sq.mm HT armored aluminum Conductor XLPE Cable of 11KV Grade (excluding supply of cable) through excavation of trench 0.6 meter wide and 1 meter deep in soft/hard soil. The cable should be placed inside heavy duty RCC Half Round Pipe of 8" inner Dia and 1 Meter length and such RCC Half Round Pipes must be placed in such a fashion so as to provide support under the cable with one half and covering over the cable with the other half.

The bed of 50mm of river sand shall be provided in the bottom of the excavated trench. The RCC Pipe shall be laid over the bed of river sand. This includes filling of gaps by fresh river sand and filling the trench upto at least 300mm height from bottom by fresh river sand. The remaining filling of the trench shall be done with the excavated stuff & should be watered and rammed properly to

its original position. The excess excavated stuff shall be disposed off from the site of work and spread in low lying areas as directed by Engineer in Charge or his nominee. The contractor shall provide heat shrinkable straight through joints of relevant size of approved make if the laying of cable shall be more than standard drum length. This includes all labour and material as directed by Engineer-in-Charge. Such cable joints shall be under the scope of work of the contractor at no extra cost or obligation from DPA. Such cable joining work is completely to be done by the contractor at his own cost.

The below figure indicates the expected arrangement of laying of cables:

Ground Level

Half round pipe Top

Half Round Pipe Bottom

1 Mtr.

Filler of Excavated Soil River Sand

0.3 Mtr.

0.6 Mtr	           Cable

Technical Specification No. 4

This includes laying of up to 3C x 240 to 400 Sq.mm HT armored aluminium Conductor XLPE Cable of 11KV Grade (excluding supply of cable) through.

- RCC Trench

The cable shall be laid after opening of RCC trench by removing the RCC Covers either through manpower or earthmover & cable trench shall be cleaned properly including removal of garbage, stones, bricks & old unused cables etc from the trench line without damaging the other cables laying in the trench. After laying of the cable, cable trench shall be properly covered with removed RCC covers as per original. The contractor shall provide heat shrinkable straight through joint of relevant size of approved make if the laying of cable shall be more than standard drum length, the straight through joint shall not be considered in the quantity of Item no. 7 & 8 of Schedule - B. This includes all labour and material as directed by Engineer-in-Charge.

- Hard & soft soil

This includes laying of cable up to 3 core 240 to 400 Sq.mm HT armored aluminum Conductor XLPE Cable of 11KV Grade (excluding supply of cable) through excavation of trench 0.6 meter wide and 1 meter deep in soft/hard soil. The cable should be placed inside heavy duty RCC Half Round Pipe of 8" inner Dia and 1 Meter length and such RCC Half Round Pipes must be placed in such a fashion so as to provide support under the cable with one half and covering over the cable with the other half.

The bed of 50mm of river sand shall be provided in the bottom of the excavated trench. The RCC Pipe shall be laid over the bed of river sand. This includes filling of gaps by fresh river sand and filling the trench upto at least 300mm height from bottom by fresh river sand. The remaining filling of the trench shall be done with the excavated stuff & should be watered and rammed properly to its original position. The excess excavated stuff shall be disposed off from the site of work and spread in low lying areas as directed by Engineer in Charge or his nominee. The contractor shall provide heat shrinkable straight through joints of relevant size of approved make if the laying of cable shall be more than standard drum length. This includes all labour and material as directed by Engineer-in-Charge. Such cable joints shall be under the scope of work of the contractor at no extra cost or obligation from DPA. Such cable joining work is completely to be done by the contractor at his own cost.

The below figure indicates the expected arrangement of laying of cables:

Ground Level

Half round pipe Top

Half Round Pipe

0.3 Mtr.

1 Mtr.

Filler of Excavated Soil

River Sand

.0.3 Mtr.

Cable

0.6Mtr

Technical Specification No. 5

Cable shall be laid underneath by using Horizontal Directional Drilling (HDD) method by putting suitable diameter HDPE pipe (suitable for cable size up to HT 3CX 400 Sq.mm having strength 10Kg/sq.cm, shall in contractor scope), The contractor shall arranged JCB Machine for excavation, water for drilling, de- watering pump, HDD equipment of 32 Ton or above capacity along with mud pump at their own cost. The cable shall be pass through heavy duty HDPE pipe buried at nominal minimum depth 165 cm or according to construction of RCC Road/ Rail network or as per directed by EIC. For single cable individual HDPE shall be pass through a road /rail crossing, for separate cable. Separate HDPE pipe shall pass through the Tunnel / trench. Laying of HDPE pipes coupled by HDPE socket only after standard length in excavated trench/tunnel and also sealing of HDPE pipe ends by suitable cap at every manhole. Back filling & dressing of excavated trenches as per specification. This includes all labour and material as directed by Engineer- in-Charge.

Technical Specification No.6

This includes laying of cable size up to 4 core x 16 to 150 Sq.mm LT armored aluminum Conductor XLPE Cable of 1.1KV Grade through.

- In RCC Trench: - The cable shall be laid after opening of RCC trench by removing the RCC Covers & cable trench shall be cleaned properly including removal of garbage, stones, bricks & old unused cables etc. from the trench line without damaging the other cables laying in the trench. After laying of the cable, cable trench shall be properly covered with removed RCC covers as per original. The contractor shall provide heat shrinkable straight through joint of relevant size of approved make if the laying of cable shall be more than standard drum length.

- Hard & soft soil

This includes laying of cable up to 4 C x 150 Sq.mm LT armored aluminum Conductor XLPE Cable of 1.1KV Grade (excluding supply of cable) through excavation of trench 0.45 meter wide and 1 meter deep in soft/hard soil. The cable should be placed inside heavy duty RCC Half Round Pipe of 6’ to 8" inner Dia (Depend on Size of Cable) and 1 Meter length and such RCC Half Round Pipes must be placed in such a fashion so as to provide support under the cable with one half and covering over the cable with the other half.

The bed of 50mm of river sand shall be provided in the bottom of the excavated trench. The RCC Pipe shall be laid over the bed of river sand. This includes filling of gaps by fresh river sand and filling the trench upto at least 300mm height from bottom by fresh river sand. The remaining filling of the trench shall be done with the excavated stuff & should be watered and rammed properly to its original position. The excess excavated stuff shall be disposed off from the site of work and spread in low lying areas as directed by Engineer in Charge or his nominee. The contractor shall provide heat shrinkable straight through joints of relevant size of approved make if the laying of cable shall be more than standard drum length. This includes all labour and material as directed by Engineer-in-Charge. Such cable joints shall be under the scope of work of the contractor at no extra cost or obligation from DPA. Such cable joining work is completely to be done by the contractor at his own cost.

The below figure indicates the expected arrangement of laying of cables:

Ground Level

Mtr.

1

Half round pipe Top

Half Round Pipe Bottom

0.45 Mtr

Filler of Excavated Soil River Sand

0.3 Mtr.

Cable

- This includes laying of cable size up to 95 sq.mm LT cable through wall/Truss/structure. Laying of single / double length cable up to 3 ½ / 4.0 core x 35 Sq.mm LT armored aluminum Conductor XLPE Cable of 1.1KV Grade on existing wall/cement structure/Truss/Perlin through PVC pipe of approved make. (Suitable for size of cable up to 95 sq. mm.) The G.I. Saddle set with base & Clamps shall be provided of suitable size (with respect to PVC pipe outer diameter) made from G.I. flat 25 x 3 mm with G.I. Nut bolts/heavy duty screws for clamping. The base shall be fixed rigidly on wall/cement structure at 0.50 Mtr. Intervals & the cable shall be laid on 3mm thick G.I. saddle base on wall/cement structure and clamped rigidly by G.I. screwing/bolting of clamps. The work includes with all materials and labour as directed by Engineer-in-charge.

Technical Specification No.7

This includes laying of cable size up to 4 core x 185 to 300 Sq.mm LT armored aluminum Conductor XLPE Cable of 1.1KV Grade through.

- In RCC Trench: - The cable shall be laid after opening of RCC trench by removing the RCC Covers & cable trench shall be cleaned properly including removal of garbage, stones, bricks & old unused cables etc. from the trench line without damaging the other cables laying in the trench. After laying of the cable, cable trench shall be properly covered with removed RCC covers as per original. The contractor shall provide heat shrinkable straight through joint of relevant size of approved make if the laying of cable shall be more than standard drum length.

- Hard & soft soil

This includes laying of cable up to 4 C x 185 to 300 Sq.mm LT armored aluminum Conductor XLPE Cable of 1.1KV Grade (excluding supply of cable) through excavation of trench 0.6 meter wide and 1 meter deep in soft/hard soil. The cable should be placed inside heavy duty RCC Half Round Pipe of 6’ to 8" inner Dia (Depend on Size of Cable) and 1 Meter length and such RCC Half Round Pipes must be placed in such a fashion so as to provide support under the cable with one half and covering over the cable with the other half.

The bed of 50mm of river sand shall be provided in the bottom of the excavated trench. The RCC Pipe shall be laid over the bed of river sand. This includes filling of gaps by fresh river sand and filling the trench upto at least 300mm height from bottom by fresh river sand. The remaining filling of the trench shall be done with the excavated stuff & should be watered and rammed properly to

its original position. The excess excavated stuff shall be disposed off from the site of work and spread in low lying areas as directed by Engineer in Charge or his nominee. The contractor shall provide heat shrinkable straight through joints of relevant size of approved make if the laying of cable shall be more than standard drum length. This includes all labour and material as directed by Engineer-in-Charge. Such cable joints shall be under the scope of work of the contractor at no extra cost or obligation from DPA. Such cable joining work is completely to be done by the contractor at his own cost.

The below figure indicates the expected arrangement of laying of cables:

Ground Level

Half round pipe Top

Half Round Pipe Bottom

1 Mtr.

0.6 Mtr

Filler of Excavated Soil River Sand

0.3 Mtr.

Cable

Technical Specification No.8

Cable shall be laid underneath by using Horizontal Directional Drilling (HDD) method by putting suitable diameter HDPE pipe (suitable for cable size up to LT 4C X 300 Sq.mm having strength 10Kg/sq.cm, shall in contractor scope), The contractor shall arranged JCB Machine for excavation, water for drilling, de- watering pump, HDD equipment’s of 32 Ton or above capacity along with mud pump at their own cost. The cable shall be pass through heavy duty HDPE pipe buried at nominal minimum depth 165 cm or according to construction of RCC Road/ Rail network or as per directed by EIC. For single cable individual HDPE shall be pass through a road /rail crossing, for separate cable. Separate HDPE pipe shall pass through the Tunnel / trench. Laying of HDPE pipes coupled by HDPE socket only after standard length in excavated trench/tunnel and also sealing of HDPE pipe ends by suitable cap at every manhole. Back filling & dressing of excavated trenches as per specification. This includes all labour and material as directed by Engineer- in-Charge.

Technical Specification No.9

- This includes supply of heat shrinkable straight through joint kit suitable for HT XLPE power cable jointing to HT 3 Core X 150 sq mm. The supply of cable joint kits as per approved make.

- This includes supply of heat shrinkable straight through joint kit suitable for HT XLPE power cable jointing to HT 3 Core X 300 sq mm. The supply of cable joint kits as per approved make.

- This includes supply of heat shrinkable straight through joint kit suitable for HT XLPE power cable jointing to HT 3 Core X 400 sq mm. The supply of cable joint kits as per approved make.

Technical Specification No.10

- This includes fixing of heat shrinkable Straight through joint suitable for flexible power cable jointing to HT 3 Core X 150 sq. mm . This including fixing of all required materials. The joint shall be made in such a way that joined section can be reeled without sagging and also joint shall be electrically and mechanically permanent. The work includes all labour, tools tackles, joint kit of approved make and as directed by

- This includes fixing of heat shrinkable Straight through joint suitable for flexible power cable jointing to 3 Core X 300 sq. mm grade. This including fixing of all required materials. The joint shall be made in such a way that joined section can be reeled without sagging and also joint shall be electrically and mechanically permanent. The work includes all labour, tools tackles, joint kit of approved make and as directed by Engineer-in-Charge.

- This includes fixing of heat shrinkable Straight through joint suitable for flexible power cable jointing to 3 Core X 400 sq. mm grade. This including fixing of all required materials. The joint shall be made in such a way that joined section can be reeled without sagging and also joint shall be electrically and mechanically permanent. The work includes all labour, tools tackles, joint kit of approved make and as directed by Engineer-in-Charge.

Technical Specification No.11

- This includes supply of heat shrinkable straight through joint kit suitable for LT 1.1 KV XLPE power Aluminium armoured cable having size up to 4 Core X 6-16 sq. mm The cable joint kits shall be supplied as per approved make.

- This includes supply of heat shrinkable straight through joint kit suitable for LT 1.1 KV XLPE power Aluminium armoured cable having size up to 4 Core X 25-50 sq. mm The cable joint kits shall be supplied as per approved make.

- This includes supply of heat shrinkable straight through joint kit suitable for LT 1.1 KV XLPE power Aluminium armoured cable having size up to 4 Core X 70-150 sq. mm The cable joint kits shall be supplied as per approved make.

- This includes supply of heat shrinkable straight through joint kit suitable for LT 1.1 KV XLPE power Aluminium armoured cable having size up to 4 Core X 185-300 sq. mm The cable joint kits shall be supplied as per approved make.

Technical Specification No.12

- This includes fixing of heat shrinkable Straight through joint suitable for LT 4 Core X 6-16 sq mm1.1 KV, Aluminium armored cable. This including fixing of all required materials. The joint shall be made in such a way that joined section can be reeled without sagging and also joint shall be electrically and mechanically permanent. The work includes all labour, tools tackles, joint kit of approved make and as directed by Engineer-in-Charge.

- This includes fixing of heat shrinkable Straight through joint suitable for LT 4 Core X 25-50 sq mm 1.1 KV, Aluminium armored cable. This including fixing of all required materials. The joint shall be made in such a way that joined section can be reeled without sagging and also joint shall be electrically and mechanically permanent. The work includes all labour, tools tackles, joint kit of approved make and as directed by by Engineer-in-Charge.

- This includes fixing of heat shrinkable Straight through joint suitable for LT 4 Core X 70-150 sq mm 1.1 KV, Aluminium armored cable. This including fixing of all required materials. The joint shall be made in such a way that joined section can be reeled without sagging and also joint shall be electrically and mechanically permanent. The work includes all labour, tools tackles, joint kit of approved make and as directed by Engineer-in-Charge.

- This includes fixing of heat shrinkable Straight through joint suitable for LT 4 Core X 185 -300 sq mm 1.1 KV, Aluminium armored cable. This including fixing of all required materials. The joint shall be made in such a way that joined section can be reeled without sagging and also joint shall be electrically and mechanically permanent. The work includes all labour, tools tackles, joint kit of approved make and as directed by by Engineer-in-Charge.

Technical Specification No.13

This include supply of following type end termination HT XLPE indoor kit as per approved make list.

- HT 3C x 70 - 95 Sq.mm cable

- HT 3C x 120 - 185 Sq.mm cable

- HT 3C x 240 - 400 Sq.mm cable

Technical Specification No.14

This include making/fixing of following type end termination HT XLPE indoor kit.

- HT 3C x 70 - 95 Sq.mm cable

- HT 3C x 120 - 185 Sq.mm cable

- HT 3C x 240 - 400 Sq.mm cable

Technical Specification No. 15

The work involves, fault finding by the cable fault locating machine in HT & LT underground cable network of various sizes by Fault finder by surge wave generator & receiver for pin point location, firm shall also arrange the pre – fault / distance locator for tracing the fault position. The equipment should be versatile to test HT & LT cables of different types, sizes and voltage levels like 11KV and 415V. The kit shall be used for cable types namely XLPE, PVC, PILC with Al / Cu conductor. The works include for restoring the healthy power on faulty cable as intimated by concerned EIC or his nominee.

The work comprise with necessary excavation work in RCC/Road/Hard & Soft soil for identify the fault is the scope of contractor by the JCB/pneumatic Breaker / excavator etc. After completion of joint work, excavated stuff shall be back filled as per its original position. Insulation Resistance value shall be measured by the contractor at both end of cable. The work include with all required Tools, Tackle, Measuring equipment, man & material & as directed by EIC.

Technical Specification No. 16

The item includes providing & fixing concealed wiring for single phase sub-circuit from the main switch/meter /DBs / MCBs to the switchboard with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 2.5 sq. mm. for phase & neutral wire and 1.5 Sq.mm continuous stranded copper conductor wire for earth to be laid through PVC Round Pipe with IS: 9537 (Part-III) of size 25 mm Diameter of Medium Mechanical Strength (MMS) type and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make. The proper size of grew shall be prepared by contractor on wall/ceiling as case may be & the conduit pipe shall be laid through prepared grew and incase of new construction the pipes shall be laid during reinforcement work. After laying of pipe the grew shall be closed with mixture of cement & sand and to match with existing surface of wall/ceiling. Complete work consists of necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 17

The item includes providing & fixing concealed wiring for single phase sub-circuit from the main switch/meter /DBs / MCBs to the switchboard with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 4 sq. mm. for phase & neutral wire and 2.5 Sq.mm continuous stranded copper conductor wire for earth to be laid through PVC Round Pipe with IS: 9537 (Part-III) of size 25 mm Diameter of Medium Mechanical Strength (MMS) type and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make. The proper size of grew shall be prepared by contractor on wall/ceiling as case may be & the conduit pipe shall be laid through prepared grew and incase of new construction the pipes shall be laid during reinforcement work. After laying of pipe the grew shall be closed with mixture of cement & sand and to match with existing surface of wall/ceiling. Complete work consists of necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 18

The item includes providing & fixing concealed wiring for light/tube/bell point from switchboard with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 1.5 sq. mm. for phase & neutral wire and 1.0 Sq.mm continuous stranded copper conductor wire for earth to be laid through PVC Round Pipe with IS: 9537 (Part-III) of size 20 mm Diameter of Medium Mechanical Strength (MMS) type and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make. The proper size of grew shall be prepared by contractor on wall/ceiling as case may be & the conduit pipe shall be laid through prepared grew and incase of new construction the pipes shall be laid during reinforcement work. After laying of pipe the grew shall be closed with mixture of cement & sand and to match with existing surface of wall/ceiling. The work also includes providing & fixing of Bell Push/Flush type SP switch 6A x 250V semi-modular Anchor Nova type or equivalant with ISI mark and to meet specifications of IS: 3854 & 3 plate Ceiling Rose/Angle Holder made from polycarbonate on suitable size of PVC box with cover. The PVC box shall be embedded properly in the wall and the switches shall be fixed on cover of the embedded box. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 19

The item includes providing & fixing concealed wiring for fan point from switchboard with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 1.5 sq. mm. for phase & neutral wire and 1.0 Sq.mm continuous stranded copper conductor wire for earth to be laid through PVC Round Pipe with IS: 9537 (Part-III) of size 20 mm Diameter of Medium Mechanical Strength (MMS) type and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make. The proper size of grew shall be prepared by contractor on wall/ceiling as case may be & the conduit pipe shall be laid through prepared grew and incase of new construction the pipes shall be laid during reinforcement work. After laying of pipe the grew shall be closed with mixture of cement & sand and to match with existing surface of wall/ceiling. The work consists providing & fixing of Flush type SP switch 6A x 250V semi-modular Anchor Nova type or equivalent with ISI mark and to meet specifications of IS: 3854, Step cut electronic fan regulator with rotary steps & 3 plate Ceiling Rose made from polycarbonate on suitable size of PVC box with cover. The PVC box shall be embedded properly in the wall and the switches shall be fixed on cover of the embedded box. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 20

The item includes providing & fixing concealed wiring for plug point with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 1.5 sq. mm. for phase & neutral wire and 1.0 Sq.mm continuous stranded copper conductor wire for earth to be laid through PVC Round Pipe with IS: 9537 (Part-III) of size 20 mm Diameter of Medium Mechanical Strength (MMS) type and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make. The proper size of grew shall be prepared by contractor on wall/ceiling as case may be & the conduit pipe shall be laid through prepared grew and incase of new construction the pipes shall be laid during reinforcement work. After laying of pipe the grew shall be closed with mixture of cement & sand and to match with existing surface of wall/ceiling. The work consists providing & fixing of Flush type SP switch 6A x 250V semi- modular with ISI mark and to meet specifications of IS: 3854, and 2 in 1 socket 6A x 250V made from polycarbonate on suitable size of PVC box with cover. The PVC box shall be embedded properly in the wall and the switch & Socket shall be fixed on cover of the embedded box. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 21

The item includes providing & fixing half point in switch board with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 1.5 sq. mm. for phase, neutral & earth. The work consists providing & fixing of Flush type SP switch 6A x 250V modular type with ISI mark and to meet specifications of IS: 3854, and 1Nos. 2 in 1 socket 5/6A x 250V made on switchboard. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge. The PVC box shall be embedded properly in the wall and the switches & Sockets shall be fixed on cover of the embedded box. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 22

The item includes providing & fixing concealed wiring for Power point with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 4.0 sq. mm. for phase & neutral wire and 2.5 Sq.mm continuous stranded copper conductor wire for earth to be laid through PVC Round Pipe with IS: 9537 (Part-III) of size 25 mm Diameter of Medium Mechanical Strength (MMS) type and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make. The proper size of grew shall be prepared by contractor on wall/ceiling as case may be & the conduit pipe shall be laid through prepared grew and incase of new construction the pipes shall be laid during reinforcement work. After laying of pipe in prepared grew the grew shall be closed with mixture of cement & sand and to match with existing surface of wall/ceiling. The work consists providing & fixing of 5 in 1 combined unit suitable for 20A & 10A with switch, socket, fuse & indicator with ISI mark. The PVC box of suitable size shall be embedded properly in the wall and the combined unit shall be fixed on embedded PVC box. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 23

The item includes providing & fixing concealed wiring for A.C point with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 4.0 sq. mm. for phase & neutral wire and 2.5 Sq.mm continuous stranded copper conductor wire for earth to be laid through PVC Round Pipe with IS: 9537 (Part-III) of size 25 mm Diameter of Medium Mechanical Strength (MMS) type and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make. The proper size of grew shall be prepared by contractor on wall/ceiling as case may be & the conduit pipe shall be laid through prepared grew and incase of new construction the pipes shall be laid during reinforcement work. After laying of pipe the grew shall be closed with mixture of cement & sand and to match with existing surface of wall/ceiling. The work also includes providing & fixing of 20A Metal clad Plug & Socket with sheet steel enclosure with ‘C’ curve SP MCB of 20A x 240V, 10 kA breaking capacity rating. The MCB shall be conforms to IS: 8828:96/IEC 60898-1:2002. The sheet steel enclosure box shall be embedded properly in the wall. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 24

The item includes providing & fixing 32 Amps. flush type DP with neon indicator for concealed wiring. The flush type 32A DP shall be wired with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 2.5 sq. mm. The work consists providing & fixing of 32 Amps. flush type DP with neon indicator with ISI mark. The PVC box of suitable size shall be embedded properly in the wall and the 32 Amps. flush type DP with neon indicator shall be fixed on PVC cover of embedded PVC box. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 25

The item includes providing & fixing surface wiring for single phase sub-circuit from the main switch /meter/DBs / MCBs to the switchboard with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 2.5 sq. mm. for phase & neutral wire and 1.5 Sq.mm continuous stranded copper conductor wire for earth to be laid through PVC Round Pipe with IS: 9537 (Part-III) of size 25 mm Diameter of Medium Mechanical Strength (MMS) type/oval shape PVC conduit pipe of 25mm and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make as directed by Engineer-in-Charge. The PVC round/oval conduit shall be fixed rigidly on wall/ceiling with suitable size heavy duty PVC saddle set with base, clamp & screw at the interval of 0.5 meter. Complete work consists of necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 26

The item includes providing & fixing surface wiring for single phase sub-circuit from the main switch /meter /DBs / MCBs to the switchboard with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 4.0 sq. mm. for phase & neutral wire and 1.5 Sq.mm continuous stranded copper conductor wire for earth to be laid through PVC Round Pipe with IS: 9537 (Part-III) of size 25 mm Diameter of Medium Mechanical Strength (MMS) type/oval shape PVC conduit pipe of 25mm and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make as directed by Engineer-in-Charge. The PVC round/oval conduit shall be fixed rigidly on wall/ceiling with suitable size heavy duty PVC saddle set with base, clamp & screw at the interval of 0.5 meter. Complete work consists of necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 27

The item includes providing & fixing surface wiring for light/tube/bell point from switchboard with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 1.5 sq. mm. for phase & neutral wire and 1.0 Sq.mm continuous stranded copper conductor wire for earth to be laid through PVC Round Pipe with IS: 9537 (Part-III) of size 20 mm Diameter of Medium Mechanical Strength (MMS) type/20mm oval shape PVC conduit pipe of 20mm and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make as directed by Engineer-in-Charge. The PVC round/oval conduit shall be fixed rigidly on wall/ceiling with suitable size heavy duty PVC saddle set with base, clamp & screw at the interval of 0.5 meter. The work consists providing & fixing of Bell Push/Flush type SP switch 6A x 250V semi modular with ISI mark and to meet specifications of IS: 3854 & 3 plate Ceiling Rose/Angle Holder made from polycarbonate on suitable size of PVC box with cover. The PVC box shall be rigidly fixed with cemented wooden gutties on the wall and the switches shall be fixed on cover of the box. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 28

The item includes providing & fixing surface wiring for fan point from switchboard with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 1.5 sq. mm. for phase & neutral wire and 1.0 Sq.mm continuous stranded copper conductor wire for earth to be laid through PVC Round Pipe with IS: 9537 (Part-III) of size 20 mm Diameter of Medium Mechanical Strength (MMS) type/20mm oval shape PVC conduit pipe and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make as directed by Engineer-in-Charge. The PVC round/oval conduit shall be fixed rigidly on wall/ceiling with suitable size heavy duty PVC saddle set with base, clamp & screw at the interval of 0.5 meter. The work consists providing & fixing of Flush type SP switch 6A x 250V semi modular with ISI mark and to meet specifications of IS: 3854, Step cut electronic fan regulator with rotary steps & 3 plate Ceiling Rose made from polycarbonate on suitable size of PVC box with cover. The PVC box shall be rigidly fixed with cemented wooden gutties on the wall and the switches shall be fixed on cover of the box. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 29

The item includes providing & fixing surface wiring for plug point with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 1.5 sq. mm. for phase & neutral wire and 1.0 Sq.mm continuous stranded copper conductor wire for earth to be laid through PVC Round Pipe with IS: 9537 (Part-III) of size 20 mm Diameter of Medium Mechanical Strength (MMS) type/20mm oval shape PVC conduit pipe and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make as directed by Engineer-in-Charge. The PVC round/oval conduit shall be fixed rigidly on wall/ceiling with suitable size heavy duty PVC saddle set with base, clamp & screw at the interval of 0.5 meter. The work consists providing & fixing of Flush type SP switch 6A x 250V semi modular with ISI mark and to meet specifications of IS: 3854, and 2 in 1 socket 5/6A x 250V made from polycarbonate on suitable size of PVC box with cover. The PVC box shall be rigidly fixed with cemented wooden gutties on the wall and the switch & Socket shall be fixed on cover of the box. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 30

The item includes providing & fixing half point in existing switch board with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 1.5 sq. mm. for phase, neutral & earth. The work consists providing & fixing of Flush type SP switch 5/6A x 250V semi modular with ISI mark and to meet specifications of IS: 3854, and 2 in 1 socket 6A x 250V made from polycarbonate on existing switchboard. The complete work consists necessary wiring connections and earth linking with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 31

The item includes providing & fixing surface wiring for plug point for computers (With 3nos. 2 in 1 socket 5/6A x 250V & 3 nos. Flush type SP switch 6A x 250V) with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 2.5 sq. mm. for phase & neutral wire and 1.5 Sq.mm continuous stranded copper conductor wire for earth to be laid through PVC Round Pipe with IS: 9537 (Part-III) of size 20 mm Diameter of Medium Mechanical Strength (MMS) type/20mm oval shape PVC conduit pipe and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make as directed by Engineer-in-Charge. The PVC round/oval conduit shall be fixed rigidly on wall/ceiling with suitable size heavy duty PVC saddle set with base, clamp & screw at the interva l of 0.5 meter. The work consists providing & fixing of 3 nos. Flush type SP switch 6A x 250V semi modular with ISI mark and to meet specifications of IS: 3854, and 3 nos. 2 in 1 socket 6A x 250V made from polycarbonate on suitable size of PVC box with cover. The PVC box shall be rigidly fixed with cemented wooden gutties on the wall and the switches & Sockets shall be fixed on cover of the box. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 32

The item includes providing & fixing surface wiring for A.C point with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 4.0 sq. mm. for phase & neutral wire and 2.5 Sq.mm continuous stranded copper conductor wire for earth to be laid through PVC Round Pipe with IS: 9537 (Part-III) of size 25 mm Diameter of Medium Mechanical Strength (MMS) type/25mm oval shape PVC conduit pipe and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make as directed by Engineer-in-Charge. The PVC round/oval conduit shall be fixed rigidly on wall/ceiling with suitable size heavy duty PVC saddle set with base, clamp & screw at the interval of 0.5 meter. The work consists providing & fixing of 20A Metal clad Plug & Socket with sheet steel enclosure with SP MCB of 20A x 240V, 10 kA breaking capacity rating. The MCB shall be conforms to IS: 8828:96/IEC 60898-1:2002. The sheet steel enclosure box shall be rigidly fixed with cemented wooden gutties on the wall. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 33

The item includes providing & fixing surface wiring for Power point with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 4.0 sq. mm. for phase & neutral wire and 2.5 Sq.mm continuous stranded copper conductor wire for earth to be laid through PVC Round Pipe with IS: 9537 (Part-III) of size 25 mm Diameter of Medium Mechanical Strength (MMS) type/25mm oval shape PVC conduit pipe and other accessories such as Tee, junction box, inspection bends, elbow etc. of approved make as directed by Engineer-in-Charge. The PVC round/oval conduit shall be fixed rigidly on wall/ceiling with suitable size heavy duty PVC saddle set with base, clamp & screw at the interval of 0.5 meter. The work consists providing & fixing of 5 in 1 combined unit suitable for 20A & 10A with switch, socket, fuse & indicator with ISI mark. The PVC box of suitable size shall be rigidly fixed with cemented wooden gutties on the wall and the combined unit shall be fixed on PVC box. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 34

The item includes providing & fixing 32 Amps. surface type DP with neon indicator for surface wiring. The surface type 32A DP shall be wired with Flame Retardant, 1100 Voltage grade, single core stranded copper conductor wire with IS: 694/1990 of size 2.5 sq. mm. The work consists providing & fixing of 32 Amps. surface type DP with neon indicator with ISI mark. The PVC box of suitable size shall be rigidly fixed with cemented wooden gutties on the wall and the 32 Amps. surface type DP with neon indicator shall be fixed on PVC cover of the PVC box. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 35

This includes supply of 4 way Double Door TPN DB as per following specification & make.

- 4 Way TPN (8 + 12 Module)

- 8 Way SPN (8 Module)

- 12 Way SPN (12 Module)

- 16 Way SPN (16 Module)

Protection device type: Main incomer: Molded case circuit breaker (MCB) - 3P or 4P Outgoing: Miniature circuit breaker (MCB) - 1P or 3P

Enclosure/Cubicle description: Double door enclosure Enclosure material: CRCA

Colour: White (RAL 9003)

Total number of 18 mm modules: 20

## Environment

- IP degree of protection IP43

- IK degree of protection IK09

Standards IS 8623-1 IS 8623-3 IEC 61439-3

Product certifications: NABL

Make: L & T/Schneider/Siemens/ABB/Hager

The DB shall be fitted with Busbar, DIN Rail and neutral link. The rates shall be excluding the cost of MCB as directed by Engineer-in-Charge.

Technical Specification No. 36

This includes fixing & commissioning of supplied double door 4 Way TPN DB on wall / structure as directed. The DB shall be fixed rigidly on wall through suitable size of nut bolts/anchor fasteners/cemented wooden gutties as directed. This includes necessary wiring, connections & earth linking with all material, labour tools & tackles as directed by Engineer-In-charge.

- 4 Way TPN (8 + 12 Module)

- 8 Way SPN (8 Module)

- 12 Way SPN (12 Module)

- 16 Way SPN (16 Module)

Technical Specification No. 37

The works include Providing & fixing chemical treated back filled compound earthing station, in Pipe for 2000 Amps (LT) capacity, complete with civil work. Marking on each earth pit coloured / painted by yellow painted on top and value also mentioned on top which less than 1 ohm. Necessary PCC chamber shall be provided surrounding earthing pit & also value of earth resistance shall be mentioned by providing and fixing of hoarding by mentioning Earth Pit ID No., Testing Date, Ohmic Valud and testing due date. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

Technical Specification No. 38

The works include supply of the following size earth strip & wire. from earth station to equipment / Main DB or as per site requirement. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in-charge.

- 12 SWG GI earthing wire

- 25X 3 Hot DIP GI strips, having minimum 80 Micron galvanized coating.

- 50X 6 Hot DIP GI strips, having minimum 80 Micron galvanized coating.

Technical Specification No. 39

This includes Laying & connecting, following size earthrthing wire & earthing strips from earth station to equipment / Main DB or as per site requirement. The complete work consists necessary wiring connections and earth linking at both the ends with all materials and labour as directed by Engineer-in- charge.

- 12 SWG GI earthing wire

- 25X 3 Hot DIP GI strips.

- 50X 6 Hot DIP GI strips.

Technical Specification No. 40

This includes supply of 20/22 Watt Round Sleek LED down Light having Robust Design with Pressure Die-Cast Alum. Housing, ensuring long life as per following technical specification.

1) Lumen: 2250 Lm

2) System Power: 20/22 Watt

3) CCT:  6500 K

4) CRI >80

5) Efficacy of >110 lm/w

6) Surge Protection: 2.5 kV

7) Input Voltage Range:  130-320 V AC

8) Beam Angle 120°

9) Optical Cover/Lens Type: Polycarbonate

10) Material:  Housing: Pressure Die Cast Aluminum

Diffuser: Polycarbonate

Clip: Steel Clip (spring)

11) Driver: Yes Included

12) Power Factor (Min): 0.95

13) Ingress Protection Code: IP 20

14) Mech. Impact Protection Code: IK02

15) Cut Out Dia. : 150 mm Maximum

16) Lamp Shaper: Round

17) Median Useful life L70B50 : 50,000 hour(s)

18) Warrantee: 2 Year

Technical Specification No. 41

This also includes fixing & commissioning of supplied 20/22 Watt Round Sleek LED Down Light Luminaries on existing false ceiling by making & providing necessary cutout of fitting dimensions and required supporting material, facilitate mounting in false ceilings as directed. The fitting shall be fixed rigidly nearby fitting through suitable size of screws/nut bolts/anchor fasteners and connections with 3 core flexible copper cable from nearest source of supply/ceiling rose & necessary connections with all material and labour and as directed by Engineer-In-charge.

Technical Specification No. 42

Fabrication work of HM Tower and LT Tower boundary with GI angle Size 75X75X10 mm with RCC Foundation technical sheet as following:

| SPECIFICATION:GI |  |
| --- | --- |
| Section | Angles |
| Classification | ISA |
| Conformity to Indian Standard | Yes |
| Product is BIS marked | Yes |
| ISI marked | Yes |
| DESIGNATION |  |
| Designation | L75X75X10 |
| Conformity to Specification | IS 1161:latest |
| Test Report: Availability of test report from central Govt./NABL/ILAC accredited lab to prove conformity to specification | Yes |

Technical Specification No. 43:

This item includes supply & fixing at site High Mast tower 30 Mtr. repair of G.I. Door of following size along with its accessories as per original:

- Size: 1460X350X3 mm.

- Size: 1070X320X3mm.

The contractor shall take prior approval of drawing from Engineer in-Charge before undertaking manufacturing of High Mast GI Door. The rate shall be inclusive of all the taxes (excluding GST), insurance, packing, forwarding, transportation, unloading at site as directed by Engineer-in-Charge.

Technical Specification No. 44:

The Technical Specifications of LED High Bay fitting is as below:

| SR.NO. | DESCRIPTION | SPECIFICATION |
| --- | --- | --- |
| 1 | Input Power of High Bay fitting | 150 Watt |
| 2 | Input voltage AC | 120-270 V AC |
| 3 | Input Frequency | 50 Hz +/-1 Hz |
| 4 | Life | 50,000 burning hours @ L70B50, Ta 35°C Outdoor |
| 5 | Mounting type for High Bay fitting | Eye bolt/Bracket for suspension mounting |
| 6 | Total Harmonic Distortion | <10% maximum |
| 7 | Working Temperature | 0°C to +45°C |
| 8 | Working Humidity | 10% to 90% RH |
| 9 | Temperature | 5700K to 6500K |
| 10 | Colour rendering index | ˃70 |
| 11 | Lumens / Watt | ≥ 120 Lumen/Watt at System Level |
| 12 | Finishing | Corrosion resistant powder coating |
| 13 | Power factor | Not less than 0.95 |
| 14 | Warranty | 5 Years from the date of successful commissioning. It is clarified that during Warranty Period, if the material is found to be defective or has poor performance or has lumen depreciation beyond permissible limit as per LM80 report, the Contractor shall promptly, Replace the material against manufacturing defects /Rectify the material, on receiving the instruction from Engineer-in-Charge at contractor's cost. The contractor shall have final & total single point responsibility for performance of the LED light fittings supplied. |
| 15 | Construction | The housing should be of single piece non-corrosive powder coated pressure die-cast alluminium frame. The weight of the High Bay fitting shall not be more than 8.0 kg. |
| 16 | Surge Protection | The Luminaire should have a 10kV SPD. The SPD should be able to sustain a minimum 15 hits of 5kA rating i.e. Total of 45 hits across all the three modes as per IEC 61000. |
| 17 | Electrical Protection | The Luminaire should be capable of withstanding voltage stress of 440V phase to phase for 8 hrs at 50 degree Celsius and should have low voltage protection as 100V for 48 hours & high voltage cut-off above 325 VAC and should have an auto restart feature. |
| 18 | Impact Resistance | IK08 |
| 19 | Driver Construction | The Drivers should be a potted driver not a printed circuit board without casing, mounted inside the luminaire. The Driver shall be of constant current type and shall have Over voltage, Over current, Over temperature & Short circuit Protection. The driver efficiency shall be more than 85%. List of make of Driver: PHILLIPS Xitanium/ MEANWELL/ OSRAM/ BAG/ SOSEN/ INVENTRONICS. Manufacturers can use their own make LED driver and the LED Driver shall be BIS certified and shall meet the specifications and comply with Safety requirements (IEC 61347-1, IEC 61347-2-13), EMC requirements (CISPR 15/ EN 55015, IEC/EN 61547, IEC/EN 61000-3-2, IEC/EN 61000-3-3). |
| 20 | Driver shall safety compliance | As per IEC 61347-1/ IS 15885 (Part2/ SEC13)/BIS certified |
| 21 | Ingress Protection Level of LED Light Fitting | IP 65 or more |
| 22 | Optics | As per Design |
| 23 | Material of optics | PC lens with toughened glass cover. The LEDs should be provided with UV resistant lens/glass cover for avoiding yellowing of the lense/glass cover. Or Exposed lensed PC Lens plate, the LEDs should be provided with anti-dust, UV resistant exposed lens for avoiding any dust & dirt accumulation on the fixtures and yellowing of the lenses. |
| 24 | Makes of LEDs | Osram, Cree, Lumileds, Nichia, Seoul. |
| 25 | Specification of LED | SMD type with wattage of each LED should be > 1 Watt and ≤ 3 Watt. |
| 26 | Certificate/Report | (1) Type test reports for LED fittings & LED Driver. (2) The luminaire should be tested as per IEC 60598 standards and following test reports should be submitted: Thermal Test, Ingress Protection Test, Electrical / Insulation Resistance Test, Endurance Test, Humidity Test. The luminaire should be tested for 'Drop test' as per IEC 60068-2-31/IS9000 Part 7 / Sec 3 standards. The luminaire should be tested for 'Vibration test' as per ANSI/IEC 68-2-6 standards. (3) Should comply to IESNA LM-79 (Approved method for the Electrical and Photometric Measurements of Solid-State Lighting Products). LM79 report from NABL accredited laboratory. (4) The LEDs used should comply to LM-80 standards (IESNA: Approved Method for Measuring Lumen Maintenance of LED Light Sources and LED lumen depreciation time to L70 based on LM-80 data). (5) The LEDs shall comply with photo biological safety norms as per IEC 62471/EN 62471/IS:16108 under Risk Group 1 (Low Risk). (6) BIS Certificate for LED Driver. (7) BIS Certificate for LED Luminaire. Contractor shall submit all the above certificate/report including BIS certificate (excluding LM79 report) for all LED light fitting at the time of supply of fittings. |

The rate shall be inclusive of all taxes (excluding GST), insurance, transportation, unloading at site as directed by Engineer in-Charge.

List of make of LED luminaire: Bajaj/ Philips/ CG/ C&S/ WIPRO/ Pyrotech/ Surya/ Nessa/ Panasonic/ Havells/ Halonix/ Orient Electric/ WMEL.

Technical Specification No. 45:

This item includes fixing & commissioning of supplied LED high bay fitting at Storage Shed. The LED high bay fitting shall be fixed on existing hanger by providing required length of SS 304 eye bolt & required accessories complete in all respect as directed by Engineer in-Charge. DPA will provide Hanger duly fixed in the Shed structure for mounting of the LED high bay fitting only. The work includes necessary wiring & connections of LED high bay fitting and 3 core, 1.5 Sq.mm braided copper flexible cable with all required material, scaffolding, labour, tools & tackles as directed by Engineer in-Charge.

Technical Specification No. 46:

Work includes supply & fixing of stainless steel hardware with washer for fixing of all the accessories & mechanical spares of panel, High mast, transformer, cables etc. Due to saline atmosphere the hardware’s got corroded after a period of time hence same are to be replaced with stainless steel.

Technical Specification No. 47:

Work includes supply & fixing of fabrication MS chequered plate hardware with washer for fixing of all the accessories & mechanical spares of etc. Due to saline atmosphere the hardware’s got corroded after a period of time hence same are to be replaced with MS chequered plate.

- Size: 1000X3000X8mm.

Note: 1) Any ancillary work arises during the execution of work, which is required to complete the work, the Contractor shall complete the item/items by carrying out such ancillary work without any extra payment.

- The work shall be carried out with entire satisfaction of Engineer-in-Charge.

Signature & Seal of Contractor	                Executive Engineer (E)

Deendayal Port Authority

# SECTION - VI

Schedule-B

| Sr. No. | Description | Qty | Unit | Rate | Amount |
| --- | --- | --- | --- | --- | --- |
| 1. | Supply at site 3 Core HT armoured aluminium conductor XLPE cable of 11KV grade of the following type & size as per IS: 7098 (Part - II) 1988 & as per Technical Specification No. 1 |  |  |  |  |
|  | - 3 Core x 150 Sq.mm (U/E) | Mtr. | 2000 |  |  |
|  | - 3 Core X 300 Sq.mm (U/E) | Mtr. | 1000 |  |  |
|  | - 3 Core X 400 sq.mm (U/E) | Mtr. | 1000 |  |  |
| 2. | Supply at site 4 Core LT armoured aluminium conductor XLPE cable of 1.1KV grade of the following type & size as per IS: 7098 (Part - I)1988 & as per Technical Specification No. 2. |  |  |  |  |
|  | - 4C X 16 Sq.mm XLPE Insulated. | Mtr. | 1000 |  |  |
|  | - 4C X 25 Sq.mm XLPE Insulated. | Mtr. | 1000 |  |  |
|  | - 4C X 35 Sq.mm XLPE Insulated | Mtr. | 1000 |  |  |
|  | - 4C X 50 Sq.mm XLPE Insulated. | Mtr. | 1000 |  |  |
|  | - 4C X 70 Sq.mm XLPE Insulated | Mtr. | 1500 |  |  |
|  | - 4C X 95 Sq.mm XLPE Insulated. | Mtr. | 1500 |  |  |
|  | - 4C X 150 Sq.mm XLPE Insulated | Mtr. | 1000 |  |  |
|  | - 4C X 300 Sq.mm XLPE Insulated | Mtr. | 1000 |  |  |
| 3. | Laying of 3C X 70 to 185 sq.mm. HT XLPE cable through the following including Testing, Termination & Commissioning as per Technical Specification No.3 |  |  |  |  |
|  | - RCC Trench cable | Mtr. | 2000 |  |  |
|  | - Hard & Soft soil | Mtr. | 1000 |  |  |
| 4. | Laying of 3C X 240 to 400 sq.mm. HT XLPE cable through the following including Testing, Termination & Commissioning as per Technical Specification No.4 |  |  |  |  |
|  | - RCC Trench cable | Mtr. | 2000 |  |  |
|  | - Hard & Soft soil | mtr. | 1000 |  |  |
| 5. | Laying of HT Cable up to 3C x 400 sq.mm through Horizontal Boring underneath RCC Road /Rail Crossing with HDPE Heavy Duty Pipe as per Technical specification No 5 | Mtr. | 1000 |  |  |
|  | - Single Length | Mtr. | 1000 |  |  |
|  | - Double Length | Mtr. | 1000 |  |  |
|  | - Triple Length | Mtr. | 500 |  |  |
| 6. | Laying of 4C x 150 sq.mm. L.T XLPE cable through the following including testing ,Termination & Commissioning of as per Technical Specification no. 6 |  |  |  |  |
|  | - Through RCC Trench | Mtr. | 3500 |  |  |
|  | - Through Hard & Soft Soil | Mtr. | 2000 |  |  |
|  | - Laying of Cable trough Wall/Trusses/Structure in PVC pipe | Mtr. | 150 |  |  |
| 7. | Laying of 4C x 185 to 300 sq.mm. L.T XLPE cable through the following including testing ,Termination & Commissioning of as per Technical Specification no. 7 |  |  |  |  |
|  | - Trough RCC Trench | Mtr. | 3500 |  |  |
|  | - Through Hard & Soft Soil | Mtr. | 3000 |  |  |
| 8. | Laying of 4C x 300 sq.mm. L.T XLPE cable through the following including testing ,Termination & Commissioning of as per Technical specification No 8 | Mtr. | 2000 |  |  |
|  | - Single Length | Mtr. | 1000 |  |  |
|  | - Double Length | Mtr. | 1000 |  |  |
|  | - Triple Length | Mtr. | 500 |  |  |
| 9. | Supply of heat shrink straight through Joint kit of 11KV XLPE 3 Core Aluminimum armoured cable of following sizes as per Technical Specification No. 9. |  |  |  |  |
|  | - HT 3C x 150 Sq. mm Cable | No. | 70 |  |  |
|  | - HT 3C x 300 Sq. mm Cable | No. | 35 |  |  |
|  | - HT 3C x 400 Sq.mm cable | No. | 35 |  |  |
| 10. | Making of heat shrink straight through Joint kit of 11KV XLPE 3 Core aluminium armoured cable of following sizes as per Technical Specification No. 10. |  |  |  |  |
|  | - HT 3C x 150 Sq.mm cable | No. | 70 |  |  |
|  | - HT 3C x 300 Sq.mm cable | No. | 35 |  |  |
|  | - HT 3C x 400 Sq.mm cable | No. | 35 |  |  |
| 11. | Supply of heat shrink straight through Joint kit of 1.1KV XLPE 4 Core Aluminimum armoured cable of following sizes as per Technical Specification No. 11. |  |  |  |  |
|  | - LT 4C X 6 – 16 Sq. mm Cable | No. | 15 |  |  |
|  | - LT 4C X 25 – 50 Sq. mm Cable | No. | 50 |  |  |
|  | - LT 4C X 70 – 150 Sq. mm Cable | No. | 25 |  |  |
|  | - LT 4C X 185 – 300 Sq. mm Cable | No. | 20 |  |  |
| 12. | Making of heat shrink straight through Joint Kit suitable for L.T. 1.1 KV XLPE 4 Core armoured cable of following size as per Technical specification No. 12 |  |  |  |  |
|  | - LT 4C X 6 – 16 Sq. mm Cable | No. | 15 |  |  |
|  | - LT 4C X 25 – 50 Sq. mm Cable | No. | 50 |  |  |
|  | - LT 4C X 70 – 150 Sq. mm Cable | No. | 25 |  |  |
|  | - LT 4C X 185 – 300 Sq. mm Cable | No. | 20 |  |  |
| 13. | Supply of Heat shrink end termination kit (Indoor Type) for 11KV 3Core H.T XLPE cable as per Technical Specification No. 13 |  |  |  |  |
|  | - HT 3C X 70 – 95 Sq. mm Cable | No. | 10 |  |  |
|  | - HT 3C X 120 – 185 Sq. mm Cable | No. | 10 |  |  |
|  | - HT 3C X 240 – 400 Sq. mm Cable | No. | 10 |  |  |
| 14. | Making of Heat shrink end termination kit (Indoor Type) for 11KV 3Core H.T XLPE cable as per Technical Specification No. 14 |  |  |  |  |
|  | - HT 3C X 70 – 95 Sq. mm Cable | No. | 10 |  |  |
|  | - HT 3C X 120 – 185 Sq. mm Cable | No. | 10 |  |  |
|  | - HT 3C X 240 – 400 Sq. mm Cable | No. | 10 |  |  |
| 15. | Locating Fault in HT & LT underground cable of various sizes by Fault Locator & route tracer Machine. As per Technical Specification No:- 15 |  |  |  |  |
|  | - HT Cable Fault | No. | 70 |  |  |
|  | - LT cable Fault | No. | 50 |  |  |
| 16. | Providing & fixing following concealed wiring for single phase sub-circuit from the main switch /Meter/ DBs /MCBs to the switch board with 2 x 2.5 sq. mm. copper conductor as per Technical Specification No. 16 | Mtr. | 1000 |  |  |
| 17 | Providing & fixing following concealed wiring for single phase sub-circuit from the main switch /Meter/ DBs /MCBs to the switch board with 2 x 4 sq. mm. copper conductor as per Technical Specification No. 17 | Mtr. | 500 |  |  |
| 18 | Providing and Fixing concealed wiring for light/tube/bell point with PVC insulated single core standard 1.5 Sq.mm. copper conductor wire as per Technical Specification No. 18 | No. | 250 |  |  |
| 19. | Providing and Fixing concealed wiring for Fan point with PVC insulated single core standard 1.5 Sq.mm. copper conductor wire & single/twin module step cut electronic fan regulator as case may be as per Technical Specification No. 19 | No. | 150 |  |  |
| 20 | Providing and fixing concealed wiring for 5/6 A X 250 Volt full plug point as per Technical Specification no. 20 | No. | 100 |  |  |
| 21 | Providing and fixing concealed wiring for 5/6A X250 Volt Half point as per Technical Specification No. 21 | no. | 200 |  |  |
| 22 | Providing and fixing concealed wiring for 15/16A X250 Volt full power point as per Technical Specification No. 22 | No. | 100 |  |  |
| 23 | Providing and fixing concealed wiring for 20A, A.C point as per Technical Specification No. 23 | No. | 25 |  |  |
| 24 | Providing and fixing concealed mounted 32 Amps. D.P. Switch as per the technical Specification No. 24 | No. | 5 |  |  |
| 25 | Providing & fixing following surface wiring for single phase sub-circuit with 2 x 2.5 sq.mm. Copper conductor from the main switch /meter. DBs / MCBs to the switch board as per Technical Specification No. 25 | Mtr. | 1000 |  |  |
| 26 | Providing & fixing following surface wiring for single phase sub-circuit with 2 x 4 sq.mm. copper conductor from the main switch /meter. DBs / MCBs to the switch board as per Technical Specification No. 26 | Mtr | 500 |  |  |
| 27 | Providing and Fixing surface wiring for light/tube/bell point with PVC insulated single core standard copper conductor wire as per technical specification No. 27 | No. | 500 |  |  |
| 28 | Providing and Fixing surface wiring for Fan point with PVC insulated single core standard 1.5 Sq.mm. copper conductor wire & single/twin module step cut electronic fan regulator as case may be as per Technical Specification No. 28 | No. | 300 |  |  |
| 29 | Providing and fixing surface wiring for 5/6 A X250 Volt plug point as per Technical Specification No. 29 | No. | 300 |  |  |
| 30 | Providing and fixing 5 pin 5/6 A X250 Volt half plug point as per Technical Specification No. 30 | No. | 200 |  |  |
| 31 | Providing and fixing surface wiring for 3 x 5/6A X250 Volt plug point with 3 nos. SP switches for computer as per Technical Specification No. 31 | No. | 150 |  |  |
| 32 | Providing and fixing surface wiring for 20A, A.C point as per technical specification No. 32. | No. | 50 |  |  |
| 33 | Providing and fixing surface wiring for 15/16A X 250Volt Power point as per Technical Specification No. 33 | No. | 250 |  |  |
| 34 | Providing and fixing surface-mounted 32 Amps.D.P. Switch Technical Specification No. 34 | No. | 25 |  |  |
| 35 | Supply of following type double door distribution board as per Technical specification No:- 35 |  |  |  |  |
|  | - 4 Way TPN (8 + 12 Module) | No. | 10 |  |  |
|  | - 8 Way SPN (8 Module) | No. | 4 |  |  |
|  | - 12 Way SPN (12 Module) | No. | 5 |  |  |
|  | - 16 Way SPN (16 Module) | No. | 4 |  |  |
| 36 | Installation of following type double door distribution board as per Technical specification No:- 36 |  |  |  |  |
|  | - 4 Way TPN (8 + 12 Module) | No. | 10 |  |  |
|  | - 8 Way SPN (8 Module) | No. | 4 |  |  |
|  | - 12 Way SPN (12 Module) | No. | 5 |  |  |
|  | - 16 Way SPN (16 Module) | No. | 4 |  |  |
| 37 | Preparation earthing station, chemical treated back filled compound earthing system with Pipe-In-Pipe 50 mm Dia GI type 3 Mtr Depth , Maintenance free as per Technical Specification No. 37. | No. | 50 |  |  |
| 38 | Supply of following type earth wire & strips for earth station as per Tech. spec. No:- 38. |  |  |  |  |
|  | - 12 SWG GI earthing wire | Mtr. | 300 |  |  |
|  | - 25X3 Hot Dip GI Strips | Mtr. | 200 |  |  |
|  | - 50 X 6 Hot Dip GI Strips | Mtr. | 200 |  |  |
| 39 | Fixing of following type earth wire for earth station to equipment’s as per requirement As per Tech. spec. No. 39. |  |  |  |  |
|  | - 12 SWG GI earthing wire | Mtr. | 300 |  |  |
|  | - 25X3 Hot Dip GI Strips | Mtr. | 200 |  |  |
|  | - 50 X 6 Hot Dip GI Strips | Mtr. | 200 |  |  |
| 40 | Supply of Round Sleek LED Down Light having Robust Design with Pressure Die-Cast Aluminum. Housing, ensuring long life as per following technical specification.40 |  |  |  |  |
|  | - 20/22 Watt LED Down Light | No. | 250 |  |  |
| 41 | Fixing & commissioning of Round Sleek LED Down Light having Robust Design with Pressure Die-Cast Aluminum. Housing, ensuring long life as per following technical specification.41 |  |  |  |  |
|  | - 20/22 Watt LED Down Light | No. | 250 |  |  |
| 42 | Fabrication of HM tower/ LT Tower boundary with RCC foundation at site 75X75X10 mm as Size GI Angles as per technical specification.42 | Kg. | 2000 |  |  |
| 43 | Repairing of GI Door of High Mast Tower 30 Mtr. with minimum 3 mm thick plate as per technical specification.43 | Kg | 200 |  |  |
| 44 | Supply at site LED High Bay fitting 150 Watt as per Technical Specification No. 44 | Nos. | 100 |  |  |
| 45 | Installation, Testing & Commissioning of LED High Bay fitting 150 Watt as per Technical Specification No. 45 | Nos. | 100 |  |  |
| 46 | Supply & fixing of miscellaneous sizes of stainless steel hardware’s of 316 grade for fixing of fixture, JB, circular rings etc., on per Kg basis and as per Technical Specification No.46 | kg | 200 |  |  |
| 47 | Supply, fixing & fabrication work of MS chequered plate as per technical specification No. 47 - Size: 1000X3000X8mm | Mtr. | 1000 |  |  |

(In word Rupees ___________________________________________________________________)

(Note: The Rates should be inclusive of all taxes, duties, fees, cess. etc. and all included charges; but exclusive of GST)

Sd-

Signature & Seal of Contractor                                                     Executive Engineer (E)

Deendayal Port Authority

Approved Make List for Electrical Items

| Sr. No. | Description | Recommended Makes |
| --- | --- | --- |
| 1 | HT VCB | SIEMENS / CROMPTON GREAVES/ABB/Schneider |
| 1(a) | HV Gas Insulated Breakers | SIEMENS /Schneider/ABB |
| 2 | POWER TRANSFORMERS | VOLTAMP/CROMPTON GREAVES /BHARAT BIJLEE/ BHEL/ SIEMENS/ ABB/ Schneider/T&R |
| 3 | DISTRIBUTION TRANSFORMERS | EMCO/KIRLOSKAR/PATSON/VOLTAMP/ ABB / Schneider / T&R |
| 4 | RESIN CAST TRANSFORMERS |  |
|  | A) RESIN CAST IMPREGNATED | VOLTAMP / KIRLOSKAR / EMCO |
|  | B) DRY CAST | VOLTAMP/KIRLOSKAR/EMCO |
| 5 | HT XLPE CABLES | POLYCAB/TORRENT/RPG ASIAN/ GLOSTER/ UNISTAR/ UNISTAR/KEI/FINOLEX/HAVELS |
| 6 | LT XLPE CABLES | POLYCAB/TORRENT/RPG ASIAN/ / RALLISON/PRIMECAB/ HAVELLS/ UNISTAR |
| 7 | LT ACB | SIEMENS/L&T/SCHNEIDER/C&S |
| 8 | PROTECTION RELAYS | AREVA/L&T/SIEMENS/ABB/C&S |
| 9 | LT PANEL | CPRI APPROVED |
| 10 | CHANGE OVER SWITCH | SIEMENS/L&T/ABB/C&S/SCHNIDER/ LEGRAND / INDOASIAN |
| 11 | SFU FOR MAIN LT DISTRIBUTION PANELS | SIEMENS/L&T/ABB/C&S |
| 12 | SFU FOR DISTRIBUTION PANELS & FEEDER PILLERS | SIEMENS/L&T/ABB/C&S/ SCHNEIDER/ LEGRAND/ INDOASIAN/HAVELLS |
| 13 | MCCB FOR MAIN LT DISTRIBUTION PANELS | SIEMENS/L&T/ABB |
| 14 | MCCB FOR DISTRIBUTION PANELS AND FEEDER PILLERS | SIEMENS/L&T/ABB/C&S/ SCHNIDER/ LEGRAND/ INDOASIAN/HAVELLS |
| 15 | MCB/ELCB/RCCB/ RCCBO FOR MAIN LT DISTRIBUTION PANELS | SIEMENS/HAGER L&T/ABB |
| 16 | MCB FOR DISTRIBUTION PANELS AND FEEDER PILLERS | SIEMENS/L&T/ABB/ SCHNEIDER/ LEGRAND/ INDOASIAN/ HAVELLS/ STANDARD |
| 17 | MCB DISTRIBUTION BOARD | STANDARD / HENSEL/LEGRAND / INDOASIAN / HAVELLS |
| 18 | MULTI FUNCTION DIGITAL METER FOR MAIN LT DISTRIBUTION PANELS/DIGITAL KWH METERS | L&T/ENERCON/SECURE/L&G/ RISHABH |

| 19 | ANALOG VOLT/AMPARE METER FOR DISTRIBUTION PANELS AND FEEDER PILLERS | RISHABH/AE/ENERCON/L&T |
| --- | --- | --- |
| 20 | SLECTOR SWITCH FOR VOLTMETER/AMPARE METER | L&T/SIEMENS/C&S |
| 21 | POWER CONTACTOR & OVER LOAD RELAYS | L&T/SIEMENS/ABB |
| 22 | QUARTZ TIME CLOCK SWITCH | L&T/INDOASIAN/SIEMENS |
| 23 | PVC WIRE WITH COPPER CONDUCTOR | RR KABEL / KEI / POLYCAB/MILEX/GUJCAB/ STANDARD / FINOLEX / ANCHOR |
| 24 | FLUSH TYPE SWITCHES, SOCKETS, HOLDERS AND CEILING ROSES & ELECTRONIC REGULATORS | ANCHOR/MK/NORTHWEST/VINAY /PANAMA / HAVELLS |
| 25 | DOOR BELLS/CALL BELLS | ANCHOR/LEGEND/MK/NORTHWEST |
| 26 | MODULAR SWITCHES, SOCKETS, PLATES & BOXES | ANCHOR / MK / NORTHWEST / LEGRAND /HAVELLs / INDOASIAN / SIMENS. |
| 27 | PVC CONDUIT/OVAL CONDUIT & CASSING CAPPING AND ACCESSORIES | PRECISION/VULCAN/FINOLEX/ GARWARE/ RESTOPLAST/ SWASTIK / BPI |
| 28 | GLS LAMPS & FLUORESCENT LAMPS | PHILIPS / BAJAJ / WIPRO / CROMPTON GREAVES / OSRAM / SURYA ROSHNI / GE |
| 29 | HPSV, HPMV & METAL HELIDE LAMPS | PHILIPS / BAJAJ / WIPRO / CROMPTON GREAVES / OSRAM / SURYA ROSHNI / GE |
| 30 | IGNITORS FOR HPSV, METAL HELIDE LAMPS | PHILIPS / BAJAJ / WIPRO / CROMPTON GREAVES / OSRAM / SURYA ROSHNI / GE |
| 31 | LUMINARIES | PHILIPS / BAJAJ / WIPRO / CROMPTON GREAVES / OSRAM / SURYA ROSHNI / GE/C&S |
| 31a | LED LUMINARIES | Philips /Bajaj/Wipro/CG/Surya/Pyrotech/Syska/Nessa/C&S having surge Protection ≥10KV for fittings & internal Surge Protection for Driver of≥4KV, LED Chip only OSRAM/CREE/Philips Lumileds/Citizen/ with LM-79,80 CERTIFICATION |
| 32 | CEILING FANS | BAJAJ/ORIENT/USHA/CROMPTON GREAVES / ALMONARD/GEC |
| 33 | WALL MOUNTING FANS | BAJAJ/ORIENT/USHA/CROMPTON GREAVES / ALMONARD/GEC |
| 34 | EXHUAST FANS | BAJAJ/ORIENT/USHA/CROMPTON GREAVES / ALMONARD/GEC |
| 35 | HEAVY DUTY INDUSTRIAL WALL MOUNTING FANS | BAJAJ/ORIENT/USHA/CROMPTON GREAVES / ALMONARD/GEC or its equivalent |
| 36 | WATER COOLER | VOLTAS/SHRIRAM USHA/BLUE STAR |
| 37 | AIR CONDITIONERS | VOLTAS/CARRIER/BLUESTAR/USHA/ HITACHI/LG/ SAMSUNG/ONIDA |

| 38 | REFRIGERATORS | VOLTAS / CARRIER / BLUESTAR / USHA / HITACHI / LG / SAMSUNG / WHIRLPOOL |
| --- | --- | --- |
| 39 | VOLTAGE STABILIZER | VEELINE / CAPRI |
| 40 | INVERTERS | SUKAM / MICROTEK |
| 41 | D.G. SETS |  |
|  | A) ENGINE | CUMMINS/GREAVES/KIRLOSKAR/ CATERPILLAR /ASHOK LEYLAND /VOLVO |
|  | B) ALTERNATOR | STAMFORD/CROMPTON GREAVES /JYOTI/ KIRLOSKAR ELECTRIC |
| 42 | ELECTRIC MOTOR | ALSTOM/CROMPTON GREAVES /SIEMENS/ KIRLOSKAR/ABB |
| 43 | WATER PUMPS | SWASTIK / KSB |
| 44 | WATER GEYSER | BAJAJ/USHA / CROMPTON GREAVES / SPHEREHOT / RACOLD |
| 45 | LUGS & CABLE GLANDS | DOWELLS / JAINSON / BRACO |
| 46 | heat shrink straight through Joint Kit | 3M |
| Note: In case of supply of Make of material which is not in the DPA approved Make list, the said material should be supplied as per the latest GETCO approved Make list. In case of supply of Make of material which is neither available in the DPA approved Make list not in the latest GETCO approved Make list, the said material should be supplied as per the Make decided by EIC for which written intimation will be given to the contractor. Before procurement of material, the Make of the material should be approved by EIC in writing. |  |  |

Seal & Sign of	Executive Engineer (E)

Contractor	  Deendayal Port Author